LMB CANopen Implementation

Used CiA (draft) standards:

- DSP-301 (version 3.0): Communication profile for Industrial Systems

- DSP-401 ( version 1.4 : Canopen  Device Profile for I/O Modules

- DSP-404 (draft 11): CANopen Device Profile for Measuring Devices and Closed-Loop Controllers -proposal

The CANopen communication protocol is a subset of the complex CAL communication protocol.

In this document only the implemented features of the CERN ATLAS DCS Local Monitoring Box are discussed.

LMB CANopen features

Following CANopen features (compare with Remote I/O Modules found in the CANopen product guide) are implemented:

| NMT Master: NMT Slave: Extended Boot-up: Minimum Boot-up: COB ID Distribution: Node ID Distribution: No. of PDOs: PDO Modes: Variable PDO Mapping: Emergency Message: Life Guarding: No. of SDOs: Device Profile: | No Yes No Yes default By jumpers internal 1 (rx) 1 (tx) asynchronous and synchronous No Yes, can be disabled Yes, Slave replies with state 1 (rx), 1(tx) CiA DSP-404 |
| --- | --- |

CANopen header

CANopen divides the 2032 available CAN message IDs or CAN object IDs (COB-IDs) into 16 functional groups (using the 4 MSB’s of the 11 bit COB-ID). The remaining 7 bits are used to identify 1 of 127 CANopen nodes.

A CANopen CAN message header will be coded as:

CAN Header

FFFF0iiiiii

| FFFF | function code (of functional group) |
| --- | --- |
| 0iiiii | 6 bit node identifier implemented by the hardware jumpers in the LMB CANmodule |

For communication the available CAN communication object identifiers (COB-IDs) are used by the LMB CANopen nodes as follows:

| Object | Function code (binary) | Resulting COB-ID | Communication parameter index in object dictionary |
| --- | --- | --- | --- |
| NMT | 0000 | 0 | - |
| SYNC | 0001 | 128 | 1005h |
| Emergency | 0001 | 129-255 | - |
| PDO1 (tx) | 0011 | 385-511 | 1800h |
| PDO1 (rx) | 0100 | 513-639 | 1400h |
| PDO2 (tx) | 0101 | 641-767 | 1801h |
| PDO2 (rx) | 0110 | 769-895 | 1401h |
| SDO (tx) | 1011 | 1409-1535 | - |
| SDO (rx) | 1100 | 1537-1663 | - |
| Nodeguard | 1110 | 1793-1919 | 100Eh |

| NMT | Network ManagemenT |
| --- | --- |
| SYNC | SYNChronisation |
| Emergency | error signalling |
| PDO | Process Data Object |
| SDO | Service Data Object |
| Nodeguard | node guarding/life guarding protocol |

This is the default COB-ID distribution, some IDs (SYNC, PDO and NODEGUARD) may be reconfigured by changing the value in the object dictionary (via the SDO).

CANopen Network ManagemenT

General

To provide for the minimum Boot-up sequence, a CANOpen slave accepts the following five different NMT messages: 
Reset_Node, Reset_Communication, Enter_Pre-Operational_State, Start_Remote_Node, Stop_Remote_Node.

At power on  the CANOpen slave (with minimum boot-up capabitity) performs a initialization sequence and enters automatically  into a  ‘Pre-Operational’ state.

In the Pre-Operational_State, the node will:

- Perform its internal I/O function

- Allow communication via the SDO channel for configuring e.g. PDO mapping, communication parameters, node guarding.

- Respond to node-guarding protocol

- Switch to:

  - Operational_ State              by the Start_Remote_Node command.

  - Prepared_ State                    by the Stop_Remote_Node command.

  - Reset the node                         by the Reset_Node or Reset_Communication commands.

In the Operational_State the node will:

- Perform its internal I/O function

- Have it’s PDO channels active (synchronized if required)

- Have it’s SDO channels active

- Send emergency messages on a error event

- Switch to:

  - Prepared_ State                   by the Stop_Remote_Node command.

  - Pre-Operational_State  by the Enter_Pre-Operational_State command.

  - Reset the node                        by the Reset_Node or Reset_Communication commands.

In the Prepared_State the node is disabled (no SDO/PDO/emergency communication) but it will:

- Perform its internal I/O function

- Switch to:

  - Pre-Operational_State  by the Enter_Pre-Operational_State command.

  - Operational_ State           by the Start_Remote_Node command.

  - Reset the node                        by the Reset_Node or Reset_Communication commands.

The NMT message format is (CAN header + 2 data bytes):

| CAN Header | Byte 1 | Byte 2 |
| --- | --- | --- |
| 000H | cs | Node_ ID |

cs  (Command Specifier) has five values according to the NMT function wanted:

| NMT function | cs ( Dec) | cs ( Hex) |
| --- | --- | --- |
| Start_Remote_Node | 1 | 01 |
| Stop_Remote_Node | 2 | 02 |
| Enter_Pre-Operational_State | 128 | 80 |
| Reset_Node | 129 | 81 |
| Reset_Communication | 130 | 82 |

Node_ID can be 1 to 127 to select a single node, or 0 to select all nodes.

The Node_ID  is defined by the hardware switch. The CANOpen slave does not send any CAN message back with these 5 NMT commands.

CANopen Synchronization

General

Synchronous transmission of a PDO means that the PDO transmission is fixed in time with respect to the transmission of the SYNC message.

Analog and digital Input nodes send their (transmit) PDO as soon as possible after the SYNC message. Output nodes update their output after the SYNC message, only if they have received their (receive) PDO in the time-period before the SYNC message (this allows for processing before updating the output, so all outputs in the system are updated at the same time). 
  
The SYNC message is a high-priority CAN message (default COB-ID is 128) with no data bytes:

CAN Header

000.1000.0000, or 080H

| COB-ID: | 128 |
| --- | --- |

CANopen Error and Emergency messages

General

The CANopen object dictionary defines three objects related to errors, 1001H (Error Register)

Object 1001H (Error Register) is a simple 8 bit status byte containing some information about all currently present errors:

| Bit | Meaning |
| --- | --- |
| 0 | Generic Error |
| 1 | Current |
| 2 | Voltage |
| 3 | Temperature |
| 4 | Communication |
| 5 | Device profile specific |
| 6 | Reserved |
| 7 | Manufacturer specific |

CANopen Node Guarding  in LMB

General

This is used to detect communication errors in the network. 
The node guarding (NMT) master can check its slaves (the 6000 series CAN nodes) and the slaves can check the master (life guarding). 
Node guarding should be used if a slave isn’t polled on a regular time base.

The object dictionary contains Node guarding configuration:

- 100CH: guard time (in milli-seconds) (not in LMB)

- 100DH: life time factor (* guard time = life time) (not in LMB)

- 100EH: node guarding identifier (default 0x700 + Node_ID) (not in LMB)

Life guarding is enabled for a slave when the node guarding master checks the slave state via a Remote Transmit Request (RTR) on the Node Guarding COB_ID, and the guard time and the life time factor are nonzero:

The NMT master message format is (CAN header with RTR):

CAN Header

111.0iii.iiii

The NMT slave replies with its current state:

| CAN Header | Byte 1 |
| --- | --- |
| 111.0iii.iiii | tsss.ssss |

| iii.iiii | Node ID |
| --- | --- |
| t | toggle bit, has to toggle every Node guarding request (1st time zero) This is not implemented in the LMB! |
| sssssss | node state: 3 = Pre-Operational 4 = Prepared 5 = Operational -> 50h LMB is waiting for ADC response 51h LMB is waiting in timing loop for time interval to finish 55h LMB is waiting for sync message |

If the node guarding master doesn’t receive the current state reply within the guard time, it signals a remote error for that slave to the application, (not in LMB)

If the slave doesn’t receive this request during its ‘life time’ (guard time * life time factor) then the slave will: (not in LMB)

- Switch to pre-operational state.

If the node guarding master restarts, it will detect the changed operational state of the slave and signal this error to the application. (not in LMB)

CANopen Service Data Objects

General

For a description of the object dictionary format and contents, see the ‘Object Dictionary Overview’.

Accessing any dictionary object can be done with the Service Data Object.

Communicating via SDO uses 2 COB-IDs:

- 600H + Node ID for master (application) to slave (6000 series CAN node)

- 580H + Node ID for slave to master

SDO uses the ‘multiplexed domain protocol’  described in de CiA DS202 standard.

A SDO access takes 2 CAN messages (master command and slave response) if the dictionary object contains no more then 4 data bytes (expedited transfer).

Any longer dictionary object is divided into (n) 7 byte segments, the transfer takes (n+1) * 2 CAN messages (segmented transfer).

The SDO over the CAN bus always contains 8 data bytes, even if not all of them are used (SDO communication is relative slow).

All CANopen numeric data is send over the CAN bus in ‘little endian’ format; multi-byte values are send with the Least Significant Byte first (e.g. Object Index or 16/32 bits object data).

Read Dictionary Object (expedited)

If an object (field) contains no more then 4 bytes of data, two CAN messages are needed to read the object:

The master (application) requests a object from the CANopen slave node with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com- mand | Object Index |  | Sub- Index | Reserved (zero) |  |  |  |

| COB-ID:110.0iii.iiii | 1536 + Node_ID |
| --- | --- |

| Command: aaabbbbb | SDO Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 010 (ccs = 2: initiate upload response) |
| bbbbb | 00000 (not used) |

The slave returns the requested object with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101.1iii.iiii | Reply | Object Index |  | Sub- Index | Data |  |  |  |

| COB-ID:1100iiiiiii | 1408 + Node_ID |
| --- | --- |

| Reply: aaabcces | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 010 (scs = 2: initiate upload response) |
| b | 0 (not used) |
| cc | (number of data bytes ([9-n to 8]) that do NOT contain data) |
| e | 1 (e=1: expedited transfer) |
| s | 1 (s = 1: data set size is indicated) |

Read Dictionary Object (segmented) (not in LMB)

If an object (field) contains more then 4 bytes of data, this data is segmented into 7 byte segments. 
After the initial request (2 CAN messages), 2 CAN messages are needed for each segment to read the object:

The master requests a object from the CANopen slave node with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com- mand | Object Index |  | Sub- Index | Reserved (zero) |  |  |  |

| COB-ID:110.0iii.iiii | 1536 + Node_ID |
| --- | --- |

| Command: aaabbbbb | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 010 (ccs = 2: initiate upload response) |
| bbbbb | 00000 (not used) |

The slave replies the request with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101.1iii.iiii | Reply | Object Index |  | Sub- Index | Length |  |  |  |

| COB-ID:110.0iii.iiii | 1408 + Node_ID |
| --- | --- |

| Reply: aaabcces | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 010 (scs = 2: initiate upload response) |
| b | 0 (not used) |
| cc | 00 (not valid) |
| e | 0 (e = 0: normal transfer) |
| s | 1 (s = 1: data set size is indicated) |

The total amount of bytes in the following transfer is indicated by the 32 bit ‘Len’ in the reply. 
Byte 5 contains the LSB, byte 8 the MSB.

All subsequent segments are transferred after a segment request from the master:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com- mand | Object Index |  | Sub- Index | Reserved (zero) |  |  |  |

| COB-ID:1100iiiiiii | 1536 + Node_ID |
| --- | --- |

| Command: aaabcccc | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 011 (ccs = 3: upload segment request) |
| b | 1/0 (toggle bit) The toggle bit must alternate for each subsequent segment request (first request has toggle bit set to 0). The slave response copies the master toggle bit. An incorrect toggle bit initiates a Abort Transfer. |
| cccc | 0000 (not used) |

The slave returns the requested segment with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101.1iii.iiii | Reply | Data |  |  |  |  |  |  |

| COB-ID:1100iiiiiii | 1408 + Node_ID |
| --- | --- |

| Reply: aaabcces | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 000 (scs = 0: upload segment respond) |
| b | 1/0 (toggle bit) |
| ccc | (number of data bytes ([9-n to 8]) that do NOT contain data) |
| e | (1 indicates last segment) |

Write Dictionary Object (expedited)

If an object (field) contains no more then 4 bytes of data, two CAN messages are needed to write the object:

The master (application) sends a object to the CANopen slave node with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com- mand | Object Index |  | Sub- Index | Data |  |  |  |

| COB-ID:110.0iii.iiii | 1536 + Node_ID |
| --- | --- |

| Command: aaabcces | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 001 (ccs = 1: initiate download request) |
| b | 0 (not used) |
| cc | (number of data bytes ([9-n to 8]) that do NOT contain data) |
| e | 1 (e=1: expedited transfer) |
| s | 1 (s = 1: data set size is indicated) |

The slave confirms the write object with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1011iiiiiii01000 | Reply | Object Index |  | Sub- Index | Reserved (zero) |  |  |  |

| COB-ID:110.0iii.iiii | 1408 + Node_ID |
| --- | --- |

| Rreply: aaabbbbb | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 011 (scs = 3: initiate download response) |
| bbbbb | 0 (not used) |

Write Dictionary Object (segmented) (not in LMB)

If an object (field) contains more then 4 bytes of data, this data is segmented into 7 byte segments. 
After the initial command (2 CAN messages), 2 CAN messages are needed for each segment to write the object:

The master initiates the write of an object to the CANopen slave node with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com- mand | Object Index |  | Sub- Index | Length |  |  |  |

| COB-ID:110.0iii.iiii | 1536 + Node_ID |
| --- | --- |

| Command: aaabcces | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 001 (ccs = 1: initiate upload response) |
| b | 0 (not used) |
| cc | 00 (not valid) |
| e | 0 (e=0: normal transfer) |
| s | 1 (s = 1: data set size is indicated) |

The total amount of bytes in the following transfer is indicated by the 32 bit ‘Len’ in the reply. 
Byte 5 contains the LSB, byte 8 the MSB.

The slave confirms the request with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101.1iii.iiii | Reply | Object Index |  | Sub- Index | Reserved (zero) |  |  |  |

| COB-ID:110.0iii.iiii | 1408 + Node_ID |
| --- | --- |

| Reply: aaabbbbb | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 011 (scs = 3: initiate upload response) |
| bbbbb | 00000 (not used) |

All subsequent segments are transferred after a segment request from the master:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com- mand | Data |  |  |  |  |  |  |

| COB-ID:110.0iii.iiii | 1536 + Node_ID |
| --- | --- |

| Command: aaabccce | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 000 scs = 0: download segment request |
| b | toggle bit. The toggle bit must alternate for each subsequent segment request (first request has toggle bit set to 0). The slave response copies the master toggle bit. An incorrect toggle bit initiates a Abort Transfer. |
| ccc | number of data bytes ([9-n to 8]) that do NOT contain data |
| e | 1 indicates last segment |

The slave confirms the segment request with:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101.1iii.iiii | Reply | Reserved (zero) |  |  |  |  |  |  |

| COB-ID:110.0iii.iiii | 1408 + Node_ID |
| --- | --- |

| Command: aaabcces | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 001 (scs = 1: download segment response) |
| B | 1/0 (toggle bit) |
| cccc | 0000 (not used) |

Abort Transfer

When an error occurs during reading/writing of a dictionary object, the slave sends a error message instead of the normal (expedited or segmented) response. 
Any abort transfer from the master to the slave just stops any further processing on the object in question.

The abort transfer messages are defined as:

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 110.0iii.iiii | Com-mand | Object Index |  | Sub-Index | Additional Code |  | Error Code | Error Class |

| COB-ID:110.0iii.iiii | 1536 + Node_ID (master to slave) |
| --- | --- |

| CAN Header | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 101.1iii.iiii | Com-mand | Object Index |  | Sub-Index | Additional Code |  | Error Code | Error Class |

| COB-ID:110.0iii.iiii | 1408 + Node_ID |
| --- | --- |

| Command: aaabbbbb | CAL Multiplexed Domain Transfer Protocol |
| --- | --- |
| aaa | 100 (scs/ccs = 4: abort domain transfer) |
| bbbbb | 00000 (not used) |

The error is explained by the Error Code (byte 7) and Error Class (byte 8), some errors need an Additional Code (byte 5 (LSB of byte 5/6))

| Description | Error Class | Error Code | Additional Code |
| --- | --- | --- | --- |
| Toggle bit not alternated (not in LMB) | 5 Service Error | 3 Parameter Inconsistent | 0 |
| Command specifier not valid | 5 Service Error | 4 Illegal Parameter | 0 |
| Object does not exist | 6 Access Error | 2 Object non-existent | 0 |
| Attempt to read a write only Object | 6 Access Error | 1 Object access unsupported | 0 |
| Attempt to write a read only Object | 6 Access Error | 1 Object access unsupported | 0 |
| Index value is reserved for further use (00A0h-0FFFh and A000h-FFFFh) | 6 Access Error | 4 Invalid address | 0 |
| Access failed due to hardware | 6 Access Error | 6 Hardware fault | 0 |
| Sub-index does not exist | 6 Access Error | 9 Object attribute inconsistent | 11h |
| Object length too high | 6 Access Error | 7 Type conflict | 12h |
| Object length too low | 6 Access Error | 7 Type conflict | 13h |
| Data cannot be transferred / Invalid signature | 8 Other Error | 0 | 20h |
| Parameter value out of range | 6 Access Error | 9 Object attribute inconsistent | 30h |
| Sub-parameter value out of range | 6 Access Error | 9 Object attribute inconsistent | 33h |
| Maximum value < Minimum value | 6 Access Error | 9 Object attribute inconsistent | 36h |
| Object cannot be mapped to PDO | 6 Access Error | 4 Invalid address | 41h |
| PDO length exceeded | 6 Access Error | 4 Invalid address | 42h |
| General internal incomptibility | 6 Access Error | 4 Invalid address | 44h |

LMB Local Monitor Box

See also:  LMB CANopen Features

Object Dictionary

Object Index:

- 1000 .. 1FFF (Communication profile Objects)

- 2000 .. 5FFF (Manufacturer Specific Objects)

- 6000 .. 9FFF (Standardized Device Profile Objects DS404)

Dictionary fields

The object dictionary table contains the following fields:

| Index | 16 bit object selection code |  |
| --- | --- | --- |
| Sub-Index | 8 bit field selection code (arrays, records) |  |
| Object Type | var | single value |
|  | array | array with same types |
|  | record | record with different types |
| Object Name | symbolic name (used in the Electronic Data Sheet) |  |
| Data Type | data type for field |  |
| Attr | rw | read and write access |
|  | wo | write only access |
|  | ro | read only access, value can change |
|  | con | read only access, value is constant |
| PDO map | Object is mappable to a PDO |  |
| Default | Factory default value for parameter |  |

Minimum / Maximum Values

Minimum/Maximum values are only given if they are different then the maximum limits for the type of object. Maximum limits are:

| Data type | Minimum value | Maximum value |
| --- | --- | --- |
| Integer8 | -128 | 127 |
| Integer16 | -32768 | 32767 |
| Integer24 | -8388608 | 8388609 |
| Integer32 | -2147483648 | 2147483647 |
| Unsigned8 | 0 | 255 |
| Unsigned16 | 0 | 65535 |
| Unsigned32 | 0 | 4294967295 |

Communication profile Objects

| Index (hex) | Sub Ndx | Object Type | Object Name | Data Type | Attr | PDO map | Default (hex) | Details |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1000 |  | var | device type | Unsigned32 | con | N | 0002 0194 | LSW = 404 (Device Profile) or 194h MSW=bit 1: device has analog inputs) |
| 1001 |  | var | error register | Unsigned8 | ro | N | 00 | see CANopen implementation details: |
| 1008 |  | var | manufacturer device name | Vis String | con | N | ' LMB' | 4 characters |
| 100A |  | var | manufacturer software version | Vis String | con | N | none | 4 characters serial number with last character M or S eg 123M or 123S |

| Index (hex) | Sub Ndx | Object Type | Object Name | Data Type | Attr | PDO map | Default (hex) | Details |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1400 |  | RECORD | receive PDO1 communication parameter |  |  | N |  |  |
| 1400 | 0 | var | number of entries | Unsigned8 | con | N | 2 |  |
| 1400 | 1 | var | COB-ID used by PDO1 (rx) | Unsigned32 | ro | N | 4000 022A example with jumpers=2A | Node-ID +4000 0200 PDO cannot be requested by a RTR see PDO description |
| 1400 | 2 | var | transmission type | Unsigned8 | ro | N | 255 | transmission type has no effect on receive PDO |
| 1401 |  | RECORD | receive PDO2 communication parameter |  |  | N |  |  |
| 1401 | 0 | var | number of entries | Unsigned8 | con | N | 2 |  |
| 1401 | 1 | var | COB-ID used by PDO2 (rx) | Unsigned32 | ro | N | C000 032A example with jumpers=2A | Node-ID +C000 0300, presently this PDO is disabled see PDO description |
| 1401 | 2 | var | transmission type | Unsigned8 | ro | N | 255 | transmission type has no effect on receive PDO |
| 1600 |  | RECORD | receive PDO1 mapping |  |  |  |  |  |
| 1600 | 0 | var | number of mapped objects | Unsigned8 | ro | N | 4 |  |
| 1600 | 1 | var | 1st receive PDO mapping | Unsigned32 | ro | N | 2201 0008 | channel 0 to 15, change ADC configuration, 8 bit code see object index 2201, length 8 |
| 1600 | 2 | var | PDO mapping | Unsigned32 | ro | N | 2202 0008 | channel 16 to 31, change ADC configuration, 8 bit code see object index 2202, length 8 |
| 1600 | 3 | var | PDO mapping | Unsigned32 | ro | N | 2203 0008 | channel 32 to 47, change ADC configuration, 8 bit code see object index 2203, length 8 |
| 1600 | 4 | var | PDO mapping | Unsigned32 | ro | N | 2204 0008 | channel 48 to 63, change ADC configuration, 8 bit code see object index 2204, length 8 |
| 1601 |  | RECORD | 2nd receive PDO2 mapping |  | ro | N |  | reserved not in use |
| 1601 | 0 | var | number of mapped objects | Unsigned8 | ro | N | 0 |  |

| Index (hex) | Sub Ndx | Object Type | Object Name | Data Type | Attr | PDO map | Default (hex) | Details |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1800 |  | RECORD | transmit PDO1 communication parameter |  |  | N |  | non mappable PDO in LMB |
| 1800 | 0 | var | number of entries | Unsigned8 | con | N | 2 |  |
| 1800 | 1 | var | COB-ID used by PDO1 (tx) | Unsigned32 | ro | N | 4000 01AA | Node-ID +140, non RTR |
| 1800 | 2 | var | transmission type | Unsigned8 | RW | N | 01 or FF | FF asynchronous rate see 6F00_1 and also 01 synch operation is accepted according to PDO transmission type table |
| 1801 |  | RECORD | transmit PDO2 communication parameter |  |  | N |  | non mappable PDO in LMB |
| 1801 | 0 | var | number of entries | Unsigned8 | con | N | 2 |  |
| 1801 | 1 | var | COB-ID used by PDO2 (tx) | Unsigned32 | ro | N | C000 02AA | Node-ID+280, presently disabled |
| 1801 | 2 | var | transmission type | Unsigned8 | ro | N | FF | according to PDO transmission type table |
| 1A00 |  | RECORD | transmit PDO1 mapping |  |  |  |  |  |
| 1A00 | 0 | var | number of mapped objects | Unsigned8 | ro | N | 4 |  |
| 1A00 | 1 | var | PDO mapping | Unsigned32 | ro | N | 6F10 0108 | channel number object index 6F10h, sub index 1, length 8 bits, channel |
| 1A00 | 2 | var | PDO mapping | Unsigned32 | ro | N | 7100 FD10 | read adc value object index 8100, sub index FD, length 16 bits |
| 1A00 | 3 | var | PDO mapping | Unsigned32 | ro | N | 6150 FD08 | read adc status,object index 6150, sub index FD, length 8 bits |
| 1A00 | 4 | var | PDO mapping | Unsigned32 | ro | N | 220X 0008 | read adc configuration byte, object index 2201 to 2204, length 8 bits channel number 0-15 = 2201, etc. |
| 1A01 |  | RECORD | transmit PDO2 mapping |  |  |  |  |  |
| 1A01 | 0 | var | number of mapped objects | Unsigned8 | ro | N | 0 | Reserved for future use |

Manufacturer Specific Objects

| Index (hex) | Sub Ndx | Object Type | Object Name | Data Type | Atrr | PDO map | Default (hex) | Details |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2100 |  | var | controller program memory | Octet String | wo | N | - | access the ATMEL flash memory (size= 2048 bytes long). NOTE 1 |  |
| 2101 |  | var | flash_cycles | Unsigned16 | ro | N | 0005 | number of times that the FLASH memory has been re-programmed. The FLASH memory can develop errors when 'flash_cycles' > 1000 |  |
| 2103 |  | var |  | Unsigned8 | rw | N | AA | Switch processor master =AA, slave |  |
| 2200 |  | var | Number of input channels | Unsigned8 | ro | N | 10, 20, 30 or 40 | Number of channels in hex or in dec 16, 32, 48 or 64 |  |
| 2201 |  | var | Configuration byte ADC#1 | Unsigned8 | rw | N | 00 | channel 0 to 15, see below. (In volatile SRAM) |  |
| 2202 |  | var | Configuration byte ADC#2 | Unsigned8 | rw | N | 00 | channel 16 to 31, see below. (In volatile SRAM) |  |
| 2203 |  | var | Configuration byte ADC#3 | Unsigned8 | rw | N | 00 | channel 32 to 47, see below. (In volatile SRAM) |  |
| 2204 |  | var | Configuration byte ADC#4 | Unsigned8 | rw | N | 00 | channel 48 to 63, see below. (In volatile SRAM) |  |
| ADC Configuration byte. Bit values. 7; 6; 5; 4; 3; 2; 1; 0; Comments; Function. 0; 0; 0; 1; Default; Conversion rate 15 Hz. 0; 0; 1; 1; Conversion rate 30 Hz. 0; 1; 0; 1; Conversion rate 60 Hz. 0; 1; 1; 1; Conversion rate 123 Hz. 1; 0; 0; 1; Conversion rate 169 Hz. 1; 0; 1; 1; Conversion rate 202 Hz. 1; 1; 0; 1; Conversion rate 4 Hz. 1; 1; 1; 1; Conversion rate 8 Hz. 0; 1; Bipolar Measurement. 1; 1; Default; Unipolar Measurement. 0; 0; 0; 1; Default; Full scale = 100 mV. 0; 0; 1; 1; Full scale = 55 mV. 0; 1; 0; 1; Full scale = 25 mV. 0; 1; 1; 1; Full scale = 1V. 1; 0; 0; 1; Full scale = 5 V. 1; 0; 1; 1; Full scale = 2.5V. 1; 1; 0; 1; Not used. 1; 1; 1; 1; Not used. |

NOTE 1: writing to object 2100h is directly into the non-volatile FLASH memory of the slace processor (no ‘store’ command needed). Erasing and programming of the FLASH memory is done by an internal background task using the ATMEL ISP feature. No other operation of the node should be executed during programming (PDOs will be ignored if they are mapped to sequence memory). After sending object 2100h, a 'reset node' NMT command should be given after suffcient delay  to restart the (new) sequences. A special file format is used and detailed description is available.

Standardised Device Profile Objects 404-11 draft 27 November 1997.

| Index (hex) | Sub Ndx | Object Type | Object Name | Data Type | Attr | PDO map | Default | Details |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 6150 Note 2 |  | array | AI_Status |  |  |  |  | Status of the analog input channels |
|  | 0 | var | Number of entries | Unsigned8 |  | N | 1 |  |
|  | 1 | var | AI_status_1 | Unsigned8 |  | Y | ... | Bit 0 measuring value not valid (bit D0 of CS5525), 1= overflow bit D1 2=not used in CS5525, bit 3 to 7 reserved) |
|  | ... | ... | ... | ... |  | ... | ... | ... |
|  | 199 | var | AI_status_199 | Unsigned8 |  | Y | ... | ... |
|  | 252 | var | Multiplexor Number | Unsigned8 |  | N | ... | ... |
|  | 253 | var | AI_Status_MUX | Unsigned8 |  | Y | 00=ok | Status Information given by mux sub index 1 |
| 6F00 |  | array | Transmission_Rate |  |  |  |  | Transmission rate for PDO 1 and 2, in 0.1ms. If non-zero then the PDO will be sent asynchronoously after a time interval elasped after the last transmission |
|  | 0 |  | Number of entries | Unsigned8 | con | N | 1 |  |
|  | 1 | var | Transmission_Rate_1 | Unsigned16 | rw | N | XX64 | xx is time between blocks of PDO1 in units of s (approx. 1 to 255s) |
| 6F10Note 2 |  | array | Multiplexer 1 |  |  |  |  | The multiplexor object allows the use of a single PDO to transport data of more than one channel in a multiplexing way. |
|  | 0 | var | Number of entries | Unsigned8 |  | N | 2 | array length, |
|  | 1 | var | Multiplexor 1 Counter | Unsigned8 |  | Y | 0 to 63 | Channel number |
| 7100 Note 2 |  | array | AI_Input_Field_Value |  |  |  |  | This object represents the converted value of an anlog input module which is not yet scaled to the physical unit of the quantity being measured. |
|  | 0 | var | Number of entries | Unsigned8 |  | N |  |  |
|  | 1 | var | Input channel 1 | Integer16 |  | N |  | ADC value for channel 1 |
|  | ... | ... | ... | ... | ... | ... |  | ... |
|  | 199 | var | Input channel 199 | Integer16 |  | N |  | ADC value for channel 199 |
|  | 252 | var | Multiplexor Number | Unsigned8 |  | N |  |  |
|  | 253 | var | AI_Input_Field_Value_MUX | Integer16 |  | Y |  | Read input channel as given by Mulitplexer 6F10 sub index 1 |

Note 2     Index  6150, 6F10 and 7100 is used by the LMB,but not accessable.

CANopen Process Data Objects

General

Accessing process parameters via SDO is relatively slow and keeps the bus busy. Normally, after the initialization of a I/O device, only the current input/output value has to be transmitted over the bus. CANOpen has defined a way to do this much faster, using a Process Data Object (PDO).

By using the PDO mapping objects (1A00H / 1A01H), the device can transmit only the actual value of an (process) object into a CAN message (the PDO). The mode of transmission is contained in the dictionary objects (1800H / 1801H).

When, for instance, the device has one 16 bit analog in- or output, this value can be mapped in the first 2 bytes of a PDO (this PDO will be two bytes long).

Because a PDO transfer does not need any confirmation, setting a 16 bit analog output just needs one CAN Message with 2 data bytes (total 60 bits over the CAN bus), instead of 2 CAN Messages with 8 data bytes (SDO, total 216 bits over the bus).

Reading a analog input can be done by a remote request of the PDO, these 2 CAN messages then take 104 bits over the bus (or the PDO can be transferred after a SYNC message, which can trigger PDOs on all devices in the net).

If a device has multiple in- or outputs, they can be mapped into a single PDO (e.g. four 16 bits analog inputs), as long as the PDO length doesn’t exceed 8 bytes (maximum of a single CAN message).

Mapping dictionary object into a PDO is done (via the SDO) using dictionary objects 1600H or 1601H (for receive PDOs of output nodes) and 1A00H or 1A01H (for transmit PDOs of input nodes).

Example of PDO mapping (analog input 16 bits and float):

| Object Dictionary Mapping |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Object | Sub Index | Value |  | Object | Sub Index | Length (in bits) | Points to: |
| 1A01 | 1 | 64010110H | = | 6401H | 01H | 10H | PDO byte 1,2 |
| 1A01 | 2 | 64040120H | = | 6404H | 01H | 20H | PDO byte 3,4,5 6 |

| PDO |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Byte 1 | Byte 2 | Byte 3 | Byte 4 | Byte 5 | Byte 6 | Byte 7 | Byte 8 |
| 6401H/LSB | 6401H/MSB | 6404H/LSB | 6404H/2nd | 6404H/3rd | 6404H/MSB | not used | not used |

The LMB does not support  (variable) PDO mapping .

When changing the PDO mapping fails (node not ‘pre-operational’, object is not mappable or PDO becomes longer then 8 bytes), the node responds with a ‘Abort domain transfer’.

PDO COB-ID

This structure gives information on  the status of the PDO of the following parameters:

bit 31 =active:  yes =  0  or no=1 
bit 30 = remote transmission request RTR allowed:  yes = 0  or no = 1 
bit 29 = how many bits in the CANbus identifier ID: 11=0  or 29=1 bits (LMB has 11 bit identifier). 
bit 28 to 11 = 0 if 11 bit ID 
bit 10 to 0 = 11 bit identifier for the particular PDO according to the profile:

| 31 | 30 | 29 | 28-11 | 10-0 |
| --- | --- | --- | --- | --- |
| 0/1 | 0/1 | 0 | 0 .0 0 0 0. 0 0 0 0. 0 0 0 0. 0 0 0 0. 0 | 11-bit Identifier |

PDO Transmission Type 
  
The transmission of a PDO can be initiated (triggered) is different ways, according to the PDO transmission type.

The options are:

- Asynchronous transmission 
The PDO can be triggered by:

  - Remote request from another device

  - Device (profile) specific event

- Synchronous transmission 
The PDO can only be triggered by the Network SYNC message, this can be done in different ways:

- Acyclic:

  - Remote request from another device ‘pre-triggers’ the PDO.

  - A device (profile) specific event ‘pre-triggers’ the PDO.

- Cyclic:

  - The PDO is triggered periodically after every (1,2, up to 240) SYNC messages.

Dictionary objects 1400H/1401H/1800H/1801H (PDO communication parameter), sub-index 2 (transmission type) determine how a PDO is triggered:

| transmission type | conditions to trigger PDO A=both needed O=one or both |  |  | PDO transmission |
| --- | --- | --- | --- | --- |
|  | Sync | RTR | Event |  |
| 0 | A |  | A | synchronous, acyclic |
| 1-240 | O |  |  | synchronous, cyclic |
| 241-251 |  |  |  | reserved |
| 252 | A | A |  | synchronous, after RTR |
| 253 |  | O |  | asynchronous, after RTR |
| 254 |  | O | O | asynchronous, manufacturer specific event |
| 255 |  | O | O | asynchronous, device profile specific event |

The DS401 I/O device profile declares the transmission type of every PDO at 255:

- transmit (input) PDOs are asynchronous, event driven (change of input) or requested with a RTR.

- receive (output) PDOs are asynchronous.

LMB implementation note

The dictionary objects 1400H/1401H/1800H/1801H (PDO communication parameter), sub-index 2 (transmission type) of the LMB is by default at 255 with the transmission time between each scanning of ADC set by the dictionary object 6F00 sub_index 1. 
It is possible to write 1 to the dictionary object 1800H, sub-index 2. The LMB then sends PDO_1  synchronous after each SYNC command. It is up to the user to ensure that the rate is not to high.

PDO inhibit time

When a PDO is triggered by a I/O event (e.g. change of digital input or reception of a RS232 character) it is possible that the PDO is triggered at such a high rate that it causes a 'traffic jam' on the CAN bus. To prevent this situation, a transmit PDO (on input nodes) has a PDO inhibit time parameter. This is a counter with a 100 µS resolution wich will inhibit the next PDO transmission for a period of time.

CANopen Electronic Data Sheet

Electronic Data Sheet

For each 6000 series CANopen node, a electronic data sheet will begenerated. This EDS is a ASCII file with general information aboutthe node and information of all dictionary object of the node.

The ASCII file is formatted like *.INI files. A sectionheader is identified with square brackets, section keywords arefollowed by ‘=’ and the value for this keyword.

In the following, the literal text of the EDS is printeditalics.

File information section

[FileInfo]

FileName=

actual file name in DOS 8.3 format, with same naming convention as node binary files (e.g. O2421100.eds)

FileVersion=

actual version number (1…255), set by creator

FileRevision=1

actual revision (1…255), changed when modified

Description=

e.g. "EDS for 6242 quad switch input"

CreationTime=

hh:mm

CreationDate=

mm-dd-yyyy

CreatedBy=

CD SYSTEMS

Following 3 keywords are not generated in new .eds files, theyshould be added when the file is modified.

| ModificationTime= | hh:mm |
| --- | --- |
| ModificationDate= | mm-dd-yyyy |
| ModifiedBy= | who done it |

General Device Information

[DeviceInfo]

VendorName=

CDSYSBV

ProductName=

4 character product name (e.g. 6242)

ProductVersion=

4 character hardware version

ProductRevision=

4 character software version

OrderCode=

up to 255 characters with ordercode

BaudRate_10=

1

BaudRate_20=

1

BaudRate_50=

1

BaudRate_100=

0 - not supported

BaudRate_125=

1

BaudRate_250=

1

BaudRate_500=

1

BaudRate_800=

0 - not supported

BaudRate_1000=

1

SimpleBootUpMaster=

0

SimpleBootUpSlave=

1 - just simple boot-up slaves…

ExtendedBootUpMaster=

0

ExtendedBootUpSlave=

0

Granularity=

8 - PDOs can map objects on a 8 bits base…

Data Type Section

| [StandardDataTypes] |  |
| --- | --- |
| 0x0001= | 1 - 1 bit boolean |
| 0x0002= | 1 - 8 bit signed integer |
| 0x0003= | 1 - 16 bit signed integer |
| 0x0004= | 1 - 32 bit signed integer |
| 0x0005= | 1 - 8 bit unsigned integer |
| 0x0006= | 1 - 16 bit unsigned integer |
| 0x0007= | 1 - 32 bit unsigned integer |
| 0x0008= | 1 - single precision floating point |
| 0x0009= | 1 - visible string |
| 0x000A= | 1 - octet string |
| 0x000B= | 0 - date |
| 0x000C= | 0 - time of day |
| 0x000D= | 0 - time difference |
| 0x000E= | 0 - bit string |
| 0x000F= | 0 - domain |
| 0x0020= | 1 - PDO CommPar |
| 0x0021= | 1 - PDO mapping |
| 0x0022= | 1 - SDO parameter |

Mapping of dummy entries (for dummy PDOmapping)

| [DummyUsage] |  |
| --- | --- |
| Dummy0001= | 0 - boolean (not mappable) |
| Dummy0002= | 1 - 8 bit signed integer |
| Dummy0003= | 1 - 16 bit signed integer |
| Dummy0004= | 1 - 32 bit signed integer |
| Dummy0005= | 1 - 8 bit unsigned integer |
| Dummy0006= | 1 - 16 bit unsigned integer |
| Dummy0007= | 1 - 32 bit unsigned integer |
| Dummy0008= | 1 - single precision floating point |

Object sections

A object is described starting with its (hexadecimal) objectnumber (e.g. [1000]). The following keywords can be used to describean object:

| SubNumber | number of sub-indices available at this index |
| --- | --- |
| ParameterName | Device profile or manufacturerer parameter name |
| ObjectType | DS301 defined object types: - 0x07 = var - 0x08 = array - 0x09 = record |
| DataType | object index of standard data type |
| LowLimit | lower limit if object is writeable |
| HighLimit | upper limit if object is writeable |
| AccessType | object access options: - const : read-only, will not change - ro : read-only, can change - wo : write-only - rw : read/writeable |
| DefaultValue | value if accesstype = const, default value after ‘restore defaults’ |
| PDOMapping | 1 = can be mapped on a PDO, 0 = not |

If a keyword (LowLimit, HighLimit, DefaultValue or PDOMapping) hasa value of zero, it may be omitted.

Mandatory dictionary objects (present inall CANopen devices)

| [MandatoryObjects] |  |
| --- | --- |
| SupportedObjects= | 0x02 - amount of mandatory objects |
| 1= | 0x1000 - device type |
| 2= | 0x1001 - error register |

Per supported object a description:

| [1000] | object index, no hexadecimal pre- or postfix |
| --- | --- |
| SubNumber= | 0 - object has no sub-index |
| ParameterName= | Device Type - object name found in DS301 |
| ObjectType= | 0x07 - VAR |
| DataType= | 0x0007 - object index of a Standard Data Type |
| AccessType= | const |
| DefaultValue= | device type number, specifies amount if device has analog / digital in/outputs + device profile number |
| PDOMapping= | 0 - object cannot be mapped on a PDO |

Optional dictionary objects (DS301 / DS401objects)

| [OptionalObjects] |  |
| --- | --- |
| SupportedObjects= | varies with amount of PDOs |
| 1= | 0x1002 - Manufacturer Status Register |
| 2= | 0x1003 - Pre-defined Error Field |
| etc… |  |

An object like 1003 is an array, this is coded as:

| [1003] |  |
| --- | --- |
| SubNumber= | 8 |
| ParameterName= | Pre-defined Error Field |

| [1003sub0] |  |
| --- | --- |
| ParameterName= | Number of Errors |
| ObjectType= | 0x07 |
| DataType= | 0x0005 |
| AccessType= | rw |
| LowLimit= | 0 - writing 0 to this object clears errors |
| HighLimit= | 8 |
| DefaultValue= |  |
| PDOMapping= | 0 |

| [1003sub1] |  |
| --- | --- |
| ParameterName= | Standard Error Field |
| ObjectType= | 0x07 |
| DataType= | 0x0007 |
| AccessType= | ro |
| etc... |  |

Manufacturer dictionary objects

This section contains the CD SYSTEMS specific object.

| [ManufacturerObjects] |  |
| --- | --- |
| SupportedObjects= |  |
| 1= | 0x20.. |
| etc. |  |